## ACS880
ACS 880 DRIVE FAILURE DATA FOR 2022 TO TILL DATE
S.NO | DRIVE DESC | RATING | DRIVE MAKE | DEPARTMENT | DIVISION | PROBLEM REPORTED | REPAIR ACTION TAKEN | FAILURE MODE | Component details
1 | ABB ACS 880 | 120A | ABB | A-FBF | IM | NOT WORKING. | PARAMETERIZATION DONE | parameterisation problem
2 | ABB ACS 880 (72 AMPERES O/P) | 72A | ABB | CRM | MU | DRIVE TRIPPING IN FAULT 5080 (COOLING FAN STUCK OR DISCONNECTED) | cooling fan replaced | Component failure | Cooling fan
3 | ACS 880 DRIVE | 60A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
4 | ACS 880 DRIVE | 90A | ABB | CRM | MU | NOT OK | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
5 | ACS 880 DRIVE 30A | 30A | ABB | CRM | MU | DC O/P NOT SHOWING. | Precharging resistor burnt | Component failure | precharging resistor
6 | ABB ACS 880 (105 A) | 105A | ABB | CRM | MU | NOT OK | FOUND VERY DUSTY, CLEANING DONE | DUST
7 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | Precharging resistor | Component failure | precharging resistor
8 | ACS 880 DRIVE (25A) | 25A | ABB | CRM | MU | OVERVOLATGE | Bleeder resistor | Component failure | Bleeder resistor
9 | ABB ACS 880 DRIVE | 25A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE IN THE DISPLAY THAN ACTUAL GENERATED DC | 330 KOHMS RESISTOR | Component failure | Bleeder resistor
10 | ABB ACS 880 | 65A | ABB | CRM | MU | TO BE CHECKED | FOUND VERY DUSTY, CLEANING DONE | DUST
11 | ABB ACS 880 DRIVE | 90A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder resistor
12 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder resistor
13 | ABB ACS 880 | 90A | ABB | GBF | IM | P/S CARD FAILURE | NA | Component failure | Diode
14 | ABB ACS 880 DRIVE | 30A | ABB | HSM | MU | NOT OK | ZINT 2A fuse blown | DC bus voltage fluctuation
15 | ABB ACS 880 DRIVE | 90A | ABB | HSM | MU | NOT WORKING | ZINT 592 CARD | Input voltage fluctuation | ZINT opto
16 | ABB ACS 880 DRIVE | 225A | ABB | HSM | MU | NOT WORKING | ZINT CARD | Input voltage fluctuation | ZINT MOSFET
17 | ABB ACS 880 DRIVE | 165A | ABB | HSM | MU | BC SHORT CIRCUITED | PARAMETERIZATION DONE | parameterisation problem
18 | ABB ACS 880 DRIVE | 90A | ABB | HSM | MU | NOT WORKING | DIODES IN P/S CARD | Component failure | Diode
19 | ABB ACS 880 DRIVE | 120A | ABB | HSM | MU | BC SHORT CIRCUITED | PARAMETERIZATION DONE | parameterisation problem
20 | ABB ACS 880 DRIVE 590 A | 590A | ABB | SP3 | IM | NOT OK | ZINT7B1C CARD | Component failure | ZINT Resistors
21 | ABB ACS880 DRIVE 105 A | 105A | ABB | CP8,9 | IM | FOR CLEANING | FOUND VERY DUSTY, CLEANING DONE | DUST
22 | ACS880 DRIVE 45 A | 45A | ABB | CP10,11 | IM | SHORT CKT | IGBT found burnt | Component failure | IGBT
23 | ACS880 DRIVE 60 A | 60A | ABB | CRM | MU | CONTROL POWER NOT COMING | Precharging resistor burnt | Component failure | precharging resistor
24 | ABB ACS880 DRIVE 110 A | 110A | ABB | HSM | MU | NOT OK | ZINP CARD | Input voltage fluctuation
25 | ABB ACS880 DRIVE (260A) | 260A | ABB | HSM | MU | DC VOLTAGE NOT OK | SCR failure | Component failure | SCR
26 | ABB ACS 880 DRIVE | 60A | ABB | CRM | MU | NOT OK | PARAMETERIZATION DONE | parameterisation problem
27 | ABB ACS 880 DRIVE | 260A | ABB | CRM | MU | NOT OK | PARAMETERIZATION DONE | parameterisation problem
28 | ACS 880 | 94A | ABB | CP8,9 | IM | NOT OK | FOUND VERY DUSTY, CLEANING DONE | DUST
29 | ACS880 DRIVE | 275 A | ABB | HSM | MU | NOT OK | ZINT CARD SMD RESISTOR | Input voltage fluctuation
30 | ACS 880 DRIVE | 60A | ABB | CRM | MU | OVERVOLTAGE | RESISTOR OF 301 KILO-OHMS | Component failure | Bleeder Resistor
31 | ACS 880 DRIVE | 144A | ABB | CP10,11 | IM | NOT OK | IGBT MODULE (WITH BGAD CARD) | Unexpected load event
32 | ACS 880 DRIVE | 32 A | ABB | CRM | MU | NOT WORKING | BRAKE CHOPPER IGBT | DC bus voltage fluctuation
33 | ACS 880 DRIVE | 32 A | ABB | CRM | MU | NO COMMUNICATION | ZCU | Component failure | ZCU
34 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
35 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
36 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
37 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
38 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
39 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
40 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
41 | ACS 880 38A | 38 A | ABB | WRM | SM | NOT OK | BRAKE CHOPPER IGBT MODULE | DC bus voltage fluctuation
42 | ACS880 DRIVE | 275 A | ABB | HSM | MU | NOT OK | ZINP-771 CARD | Input voltage fluctuation
43 | ACS 880 REGENERATIVE DRIVE | 430 A | ABB | NOAMUNDI | NOAMUNDI | NOT OK | 3 NUMBERS OF PRECHARGING RESISTORS, CONTACTOR | Dust
44 | ACS 880 REGENERATIVE DRIVE | 430 A | ABB | NOAMUNDI | NOAMUNDI | NOT OK | 3 NUMBERS OF PRECHARGING RESISTORS, CONTACTOR | Dust
45 | ABB ACS880-01-105A | 105 A | ABB | CRM | MU | 24v supply was fluctuating issue with ZCU |  | Component failure | ZCU
46 | ABB Drive 880-01-105A | 105 A | ABB | CRM | MU | DC Voltage was ok but showing Zero through Measuring Card(ZINT) |  | Component failure | ZINT Resistors
47 | ACS880-01-246A | 246 A | ABB | CRM | MU | fault 5081 Auxilary fan1 not working |  | Component failure | Cooling Fan
48 | ABB Drive 880-01-226A-3 | 226 A | ABB | CRM | MU | "PU State feedback Fault" 5696 was appearing |  | Component failure | ZINT Reistors
49 | ACS880-01-145A-3 | 145 A | ABB | CRM | MU | No Communication between drive and CDP |  | Component failure | Ribbon Cable
50 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
51 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
52 | ACS880-635A-05 | 635 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT Fuse
53 | ACS880-246A-03 | 246 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT Mosfet
54 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
55 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
56 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
57 | ACS880-820A-03 | 240 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
58 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
59 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
60 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
61 | ACS880 | 980A | ABB | SP3 | IM | SCF 6024 tripped in Short circuit fault |  | Component failure | IGBT
62 | ACS880-104-0760A-3+C188 | 760 A | ABB | CP10,11 | IM | Memory Unit was found faulty and crane firmware was corrupted. |  | Firmware corrupt
63 | ACS880-104-0760A-3+C188 | 760 A | ABB | CP10,11 | IM | IGBT unit Failed – 2 times in different module. |  | Component failure | IGBT

## Department wise
Plant | Nos
CRM | 22
HSM | 21
WRM | 8
CP10,11 | 4
SP3 | 2
NOAMUNDI | 2
CP8,9 | 2
A-FBF | 1
GBF | 1
Grand Total | 63

## CRM Failure Mode
Failure Mode | Nos
Component failure | 17
DUST | 2
parameterisation problem | 2
DC bus voltage fluctuation | 1
Grand Total | 22

## CRM Component FM
Component Details | Nos
Bleeder Resistor | 7
precharging resistor | 3
ZCU | 2
Cooling fan | 2
ZINT Reistors | 1
ZINT Resistors | 1
Ribbon Cable | 1
Grand Total | 17

## CRM Component FM (hidden)
S.NO | DRIVE DESC | RATING | DRIVE MAKE | DEPARTMENT | DIVISION | PROBLEM REPORTED | REPAIR ACTION TAKEN | FAILURE MODE | Component details
49 | ACS880-01-145A-3 | 145 A | ABB | CRM | MU | No Communication between drive and CDP |  | Component failure | Ribbon Cable
2 | ABB ACS 880 (72 AMPERES O/P) | 72A | ABB | CRM | MU | DRIVE TRIPPING IN FAULT 5080 (COOLING FAN STUCK OR DISCONNECTED) | cooling fan replaced | Component failure | Cooling fan
3 | ACS 880 DRIVE | 60A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
4 | ACS 880 DRIVE | 90A | ABB | CRM | MU | NOT OK | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
5 | ACS 880 DRIVE 30A | 30A | ABB | CRM | MU | DC O/P NOT SHOWING. | Precharging resistor burnt | Component failure | precharging resistor
23 | ACS880 DRIVE 60 A | 60A | ABB | CRM | MU | CONTROL POWER NOT COMING | Precharging resistor burnt | Component failure | precharging resistor
7 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | Precharging resistor | Component failure | precharging resistor
8 | ACS 880 DRIVE (25A) | 25A | ABB | CRM | MU | OVERVOLATGE | Bleeder resistor | Component failure | Bleeder Resistor
9 | ABB ACS 880 DRIVE | 25A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE IN THE DISPLAY THAN ACTUAL GENERATED DC | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
30 | ACS 880 DRIVE | 60A | ABB | CRM | MU | OVERVOLTAGE | RESISTOR OF 301 KILO-OHMS | Component failure | Bleeder Resistor
11 | ABB ACS 880 DRIVE | 90A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
12 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
48 | ABB Drive 880-01-226A-3 | 226 A | ABB | CRM | MU | "PU State feedback Fault" 5696 was appearing |  | Component failure | ZINT Reistors
47 | ACS880-01-246A | 246 A | ABB | CRM | MU | fault 5081 Auxilary fan1 not working |  | Component failure | Cooling fan
46 | ABB Drive 880-01-105A | 105 A | ABB | CRM | MU | DC Voltage was ok but showing Zero through Measuring Card(ZINT) |  | Component failure | ZINT Resistors
45 | ABB ACS880-01-105A | 105 A | ABB | CRM | MU | 24v supply was fluctuating issue with ZCU |  | Component failure | ZCU
33 | ACS 880 DRIVE | 32 A | ABB | CRM | MU | NO COMMUNICATION | ZCU | Component failure | ZCU

## CRM Failures (hidden)
S.NO | DRIVE DESC | RATING | DRIVE MAKE | DEPARTMENT | DIVISION | PROBLEM REPORTED | REPAIR ACTION TAKEN | FAILURE MODE | Component details
49 | ACS880-01-145A-3 | 145 A | ABB | CRM | MU | No Communication between drive and CDP |  | Component failure | Ribbon Cable
2 | ABB ACS 880 (72 AMPERES O/P) | 72A | ABB | CRM | MU | DRIVE TRIPPING IN FAULT 5080 (COOLING FAN STUCK OR DISCONNECTED) | cooling fan replaced | Component failure | Cooling fan
3 | ACS 880 DRIVE | 60A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
4 | ACS 880 DRIVE | 90A | ABB | CRM | MU | NOT OK | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
5 | ACS 880 DRIVE 30A | 30A | ABB | CRM | MU | DC O/P NOT SHOWING. | Precharging resistor burnt | Component failure | precharging resistor
6 | ABB ACS 880 (105 A) | 105A | ABB | CRM | MU | NOT OK | FOUND VERY DUSTY, CLEANING DONE | DUST
7 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | SHOWING INCORRECT DC BUS VOLTAGE | Precharging resistor | Component failure | precharging resistor
8 | ACS 880 DRIVE (25A) | 25A | ABB | CRM | MU | OVERVOLATGE | Bleeder resistor | Component failure | Bleeder Resistor
9 | ABB ACS 880 DRIVE | 25A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE IN THE DISPLAY THAN ACTUAL GENERATED DC | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
10 | ABB ACS 880 | 65A | ABB | CRM | MU | TO BE CHECKED | FOUND VERY DUSTY, CLEANING DONE | DUST
11 | ABB ACS 880 DRIVE | 90A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
12 | ABB ACS 880 DRIVE | 120A | ABB | CRM | MU | DC VOLTAGE SHOWING MORE THAN THE ACTUAL GENERATED | 330 KOHMS RESISTOR | Component failure | Bleeder Resistor
48 | ABB Drive 880-01-226A-3 | 226 A | ABB | CRM | MU | "PU State feedback Fault" 5696 was appearing |  | Component failure | ZINT Reistors
47 | ACS880-01-246A | 246 A | ABB | CRM | MU | fault 5081 Auxilary fan1 not working |  | Component failure | Cooling fan
46 | ABB Drive 880-01-105A | 105 A | ABB | CRM | MU | DC Voltage was ok but showing Zero through Measuring Card(ZINT) |  | Component failure | ZINT Resistors
45 | ABB ACS880-01-105A | 105 A | ABB | CRM | MU | 24v supply was fluctuating issue with ZCU |  | Component failure | ZCU
33 | ACS 880 DRIVE | 32 A | ABB | CRM | MU | NO COMMUNICATION | ZCU | Component failure | ZCU
32 | ACS 880 DRIVE | 32 A | ABB | CRM | MU | NOT WORKING | BRAKE CHOPPER IGBT | DC bus voltage fluctuation
30 | ACS 880 DRIVE | 60A | ABB | CRM | MU | OVERVOLTAGE | RESISTOR OF 301 KILO-OHMS | Component failure | Bleeder Resistor
27 | ABB ACS 880 DRIVE | 260A | ABB | CRM | MU | NOT OK | PARAMETERIZATION DONE | parameterisation problem
26 | ABB ACS 880 DRIVE | 60A | ABB | CRM | MU | NOT OK | PARAMETERIZATION DONE | parameterisation problem
23 | ACS880 DRIVE 60 A | 60A | ABB | CRM | MU | CONTROL POWER NOT COMING | Precharging resistor burnt | Component failure | precharging resistor

## HSM FM
Failure Modes | Nos
Component failure | 13
Input voltage fluctuation | 5
parameterisation problem | 2
DC bus voltage fluctuation | 1
Grand Total | 21

## HSM Component FM
Row Labels | Count of S.NO
IGBT | 6
ZCU | 3
ZINT fuse | 1
ZINT MOSFET | 1
Diode | 1
SCR | 1
Grand Total | 13

## Sheet9 (hidden)
S.NO | DRIVE DESC | RATING | DRIVE MAKE | DEPARTMENT | DIVISION | PROBLEM REPORTED | REPAIR ACTION TAKEN | FAILURE MODE | Component details
60 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
59 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
58 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
57 | ACS880-820A-03 | 240 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
56 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
55 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
54 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
53 | ACS880-246A-03 | 246 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT MOSFET
52 | ACS880-635A-05 | 635 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT fuse
51 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
50 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
25 | ABB ACS880 DRIVE (260A) | 260A | ABB | HSM | MU | DC VOLTAGE NOT OK | SCR failure | Component failure | SCR
18 | ABB ACS 880 DRIVE | 90A | ABB | HSM | MU | NOT WORKING | DIODES IN P/S CARD | Component failure | Diode

## HSM Failures (hidden)
S.NO | DRIVE DESC | RATING | DRIVE MAKE | DEPARTMENT | DIVISION | PROBLEM REPORTED | REPAIR ACTION TAKEN | FAILURE MODE | Component details
60 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
59 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
58 | ACS880-240A-05 | 240 A | ABB | HSM | MU | ZCU not communicating. Drive tripped on Task overload fault |  | Component failure | ZCU
57 | ACS880-820A-03 | 240 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
56 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
55 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
54 | ACS880-820A-03 | 820 A | ABB | HSM | MU | Flash over in drive inverter section |  | Component failure | IGBT
53 | ACS880-246A-03 | 246 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT MOSFET
52 | ACS880-635A-05 | 635 A | ABB | HSM | MU | ZINT card Failed |  | Component failure | ZINT fuse
51 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
50 | ACS880-880A-05 | 880 A | ABB | HSM | MU | Drive tripping in SC fault-2340 |  | Component failure | IGBT
42 | ACS880 DRIVE | 275 A | ABB | HSM | MU | NOT OK | ZINP-771 CARD | Input voltage fluctuation
29 | ACS880 DRIVE | 275 A | ABB | HSM | MU | NOT OK | ZINT CARD SMD RESISTOR | Input voltage fluctuation
14 | ABB ACS 880 DRIVE | 30A | ABB | HSM | MU | NOT OK | ZINT 2A fuse blown | DC bus voltage fluctuation | ZINT fuse
15 | ABB ACS 880 DRIVE | 90A | ABB | HSM | MU | NOT WORKING | ZINT 592 CARD | Input voltage fluctuation | ZINT opto
16 | ABB ACS 880 DRIVE | 225A | ABB | HSM | MU | NOT WORKING | ZINT CARD | Input voltage fluctuation | ZINT MOSFET
17 | ABB ACS 880 DRIVE | 165A | ABB | HSM | MU | BC SHORT CIRCUITED | PARAMETERIZATION DONE | parameterisation problem
18 | ABB ACS 880 DRIVE | 90A | ABB | HSM | MU | NOT WORKING | DIODES IN P/S CARD | Component failure | Diode
19 | ABB ACS 880 DRIVE | 120A | ABB | HSM | MU | BC SHORT CIRCUITED | PARAMETERIZATION DONE | parameterisation problem
25 | ABB ACS880 DRIVE (260A) | 260A | ABB | HSM | MU | DC VOLTAGE NOT OK | SCR failure | Component failure | SCR
24 | ABB ACS880 DRIVE 110 A | 110A | ABB | HSM | MU | NOT OK | ZINP CARD | Input voltage fluctuation